## Slide 1: Texas Gas Transmission, LLC Presentation for the Commonwealth of Kentucky Legislature
February 2, 2023

## Slide 2: Texas Gas Overview
Major offices in Owensboro, KY and Houston, TX
303 employees in Kentucky
Approximately 1200 employees system-wide and 200 employees in Owensboro
Almost 1500 miles of pipelines in Kentucky
Approximately 78 Billion cubic feet of natural gas storage capacity in Kentucky
Texas Gas contributed over $7.8 Million in ad valorem taxes to Kentucky in 2022

## Slide 3: System Map

## Slide 4: Services Provided by Texas Gas
Texas Gas performs its transportation services in accordance with customer’s requests, on a daily basis, and is regulated by the Federal Energy Regulatory Commission
Texas Gas Transmission is an open-access, interstate pipeline providing transportation and storage services for customers.
  Services for customers
    Transporting and storing customer gas
    Customers choose type of service
      Firm or Interruptible Transportation
      Firm or Interruptible Storage
      No Notice Service

## Slide 5: Kentucky and Indiana

## Slide 6: System Performance
Day 1 – Day 5 of each storm - normalized to Dec 2022 Winter Storm Elliot

## Slide 7: Preparation and What Happened
Steps taken in advance of the storm
  Winterized critical equipment
  Added natural gas and pressure to the north end of the system
  Manned key compression stations/locations
What happened during the storm
  On the morning of December 23, 2022, TXG Gas Control Center requested to start horsepower at Slaughters Station
  Control unit on a valve failed due to icing
    This affected our ability to deliver gas to KU’s electric generation plants at contractual pressures, which limited their ability to bring on all of their generation.
    This component failure did not prevent Texas Gas’ ability to source 1.62 Billion cubic feet per day of storage capacity from storage fields in KY and IN to replace lost supply.

## Slide 8: Steps We Have Taken
Immediate near-term action steps across the system
  Additional maintenance checks on control and other critical equipment prior to severe winter weather events
  Additional temporary covers and heating equipment on critical equipment that is exposed to the elements
  Work with our control center to turn on compression and run it in a bypass or unloaded condition so it will be ready for full load when needed
Additional action steps
  Fabricate and install permanent structures over certain critical control equipment and include appropriate heat equipment